## Slide 1: Control principles and guidelines@MAXIV
KITS Control and Acquisition mini workshop, KITS

## Slide 2
04/28/10
What is Tango?
Provides a unified interface to all equipments, hiding how they are connected to a computer (serial line, USB, sockets….)
Hide the network
Location transparency
Tango is one of the Control System available today but other exist (EPICS…)

## Slide 3
Distributed control system
Standard Interface
Modular
Comes with many tools
Well supported by the synchrotron community
Companion frameworks

## Slide 4: TANGO : introduction
Machine A
SE1
Application 1
Application 2
Lµ
Lb
Machine B
Application 4
Lb
Application 3
Lb
SE2
?
?
?

## Slide 5: TANGO : introduction
Machine A
Application 1
Application 2
Machine B
Application 3
Application 4
Lµ
Lb
Lb
Lb
SE1
SE2

## Slide 6: TANGO : introduction
Machine A
Application 1
Application 2
Machine B
Application 3
Application 4
Lµ
Lb
Lb
Lb
SE1
SE2

## Slide 7: TANGO : introduction
Machine A
Application 1
Application 2
Machine B
Application 3
Application 4
Lµ
Lb
Lb
Lb
SE1
SE2

## Slide 8: TANGO : introduction
Machine A
Application 1
Application 2
Machine B
Application 3
Application 4
Lµ
Lb
Lb
Lb
SE1
SE2

## Slide 9: TANGO : introduction
Distributed Application

## Slide 10: TANGO : introduction

## Slide 11: TANGO : introduction

## Slide 12: TANGO : introduction

## Slide 13: TANGO : introduction

## Slide 14: TANGO : introduction

## Slide 15: TANGO : introduction
TANGO
(CORBA based)
A standard tool in charge of the communications between software components making up distributed and heterogeneous applications

## Slide 16: TANGO : device : interface
Has a communication interface
  interface device <=> class
  interface = commands + attributes
    commands » actions
    attributes » physical units
Implementation/Realisation
Interface
Commands
attributes
Generics
Specifics
Generics
Specifics
public
privé
Init
State
Status
PowerOn
PowerOff
-
current

## Slide 17: A Tango Device Class (example)
04/28/10
A ski lift class
  3 states
    ON, OFF, FAULT (OFF at startup)
  3 commands
  3 attributes
Name | In | Out | Allowed
Reset | Void | Void | If FAULT
On | Void | Void | If NOT FAULT
Off | Void | Void | Always
Name | type | format | Writable
Speed | double | scalar | Read/Write
Wind_speed | double | scalar | Read
Seats_pos | long | spectrum | Read

## Slide 18: TANGO : device : summary
Device
Generic
Behavior
properties
ens-[seg]/dom/elem.1
ens-[seg]/dom/elem.2
ens-[seg]/dom/elem.3
Where to store the properties and all the configuration data ?
Instantiation
My Device
Commands
attributes
Status
Classe
ID Unique

## Slide 19: Archiving Performance polling vs cache/event
Tango Device
Hardware
Current
Voltage
Resistance
Interlocked
…
Hardware
performance =
100 requests/s
Tango device performance =
< 100 requests/s
Polling Case:
Short Term DB
Long Term DB

## Slide 20: Archiving Performance: polling vs cache/event
Tango Device
Hardware
Current | 2.4
Voltage | 4.81
Resistance | 2
Interlocked | FALSE
Output | ON
… | 
events
Cache polling fit bandwidth
Hardware
performance =
100 request/s
80 Hz (80% of 100)
Tango
Performance =
10000 request/s
+ events
Cache/Event Case:
Short Term DB
Long Term DB
Drawback: Accept delay in answer

## Slide 21: Properties
Settings to initialise the device

## Slide 22: Attributes
Physical parameters of the device

## Slide 23: Commands
Physical actions of the device

## Slide 24: Verticale “Lasagna” layers

## Slide 25
Beamline’s Control System

## Slide 26: Database - Jive

## Slide 27: PLC system example
PLC
PLC
TCO
Gauge
Valv
Heat Absorber
…
TCO
- Temperature
Gauge
- Pressure
Valv
Insert
Extract
Ion Pump
- Pressure
GammaSPCe
Ion Pump
High Level
Device
Low level
Device
Hardware
Controller
Hardware

## Slide 28
SOFTWARE | User Interface |  |  | 
 | Computation Layer |  |  | 
 | Hardware Layer |  |  | 
HARDWARE |  |  |  | 
Components
DAQ
icepap
Mono
Undulator
DAQ
Acquisition

## Slide 29: Naming convention
Device name follows the MAX IV standard naming convention
Alias can be define within a custom beamline convention
Some alias are generated from the motor spreadsheet

## Slide 30: Python Client interface
# Set the attribute transparently
pilatus.filename = ‘/data/visitor/beammax/…’
pilatus.framePeriod = 0.1
pilatus.exposureTime = 0.05
pilatus.frameNumber = 200
pilatus.triggerMode = “EXTERNAL_MULTI"
# Connection to a remote device
pilatus = DeviceProxy(‘bsp02-e/dia-detpi-01’)

## Slide 31: Python Client interface
# Execute action
pilatus.acquire()
# At any time the state should known
# ON, STANDBY, RUNNING, …
pilatus.state()

## Slide 32: Intranet Of Things
 | Accelerators | Biomax
Host | 168 | 15
Process | 1945 | 77
Device | 12392 | 705
Control Point | 491079 | 24501
Class of device | 170 | 50
attributes | 234631 | 10500
commands | 130251 | 7717
MAX IV = 700 000 control points

## Slide 33: IT Infrastructure
Core Switch
Access switch 40Gbit
Access switch
VM
VM
VM
VM
VM
VM
redundant 2+2
32*6 core Intel Xeon
16 TB ram
4*40Gbit
Ethernet
Access switch
Latency ± 300 us

## Slide 34: Tango Servers - Astor
Process managing one or more devices
Start, Stop, Restart, Change host
Statistics: uptime, reliability, …

## Slide 35: From complex to usable
500K
25K
Accelerator
Beamline
Data collection
scan e 200 1000 1

## Slide 36: Guideline
Only report/control the strict minimum
The hardware can run without the Tango device
The Tango device should NOT change the state of the equipment at the initialisation
  Exception: memorised attributes
SOC, Separation of Concern ~ Single Responsibility
Stay alive to report hardware failure
Init command to recover a connection (Not restart)
Stay in FAULT in case of problem, Acknowledge via the Init command
Avoid automatic reconnection

## Slide 37: Guideline
Complex device should be split into several
Integration instead of reinventing the wheel
Reusable over specific