## Slide 1: Alarm Handling
Selection and configuration of alarms based on operational modes. Alarm Acknowledgment Policy.
Jorick Lochet – Automation engineer – Integrated Control System section at ESS

## Slide 2: Agenda
1 Introduction : Control systems in ESS
2 The role of alarms
3 Challenges

## Slide 3: Introduction
Control systems at ESS
EPICS: framework for building distributed control systems. It is designed to handle the control and monitoring of various devices and processes in a modular and scalable manner.
EPICS provides the infrastructure for managing hardware interfaces, data acquisition, and control algorithms.
CS Studio offers Operator Interfaces (OPI) to present data in a user-friendly format, provides features such as trends, alarms, and visual representation of historical data.

## Slide 4
Layer architecture of ESS control systems
ESS Main Control Room
Experiment workstations
other human interfaces
EPICS
Timing System
Fieldbus
Personnel Safety Systems
H2O Flow
He Flow
RF
Proton
Neutron
Temp
Electricity
Mech. Movement
Machine Protection
Device signals
Remote
I/O
Controller
PLC
EPICS
IOC
EPICS
IOC
Controller
etc.
PLC
MicroTCA
System
Ether
CAT
MicroTCA
System
Remote
I/O
Alarms
EPICS
IOC
Config.
Tools
Device
Electronics
Remote
I/O
Data on
Demand
Event
Generator
Fast Beam
Interlock System
PSS
PLC
Chopper
Power Supply
Sensor
Motor
Pump
Flowmeter
PSS
GUIs
Device
Electronics
Switch
Sensor
Sensor
EPICS
IOC
EPICS
IOC
Archiver
Magnetic
Equipment
OPI
Alarm Server
Techncal Network
Notes: User interface : Live database, archiver database, alarm server and let the information to the disposal for the OPI
Communicate with PLC through an IOC (Input Output Controller) = like a software controller – The frontier between the PLC and the databases
IOC(s) – Input output controller that receives data and make them available on the epics environment layer
PLC / remote IO to control and receive data from field objects

## Slide 5: The role of alarms
Critical for monitoring and controlling processes :
Prevent accidents: For example, in a cryogenics environment, oxygen deficiency alarms can prevent accidents by alerting operator to dangerous level of oxygen.
Reduce downtime: In a manufacturing facility, equipment malfunction alarms can help identify issues early, reducing costly downtime for repairs.
Ensure compliance: Alarms can help ensure that processes adhere to safety and environmental regulations. For instance, an alarm may indicate when emissions exceed permissible limits in a power plant.
Notes: Alarms are crucial signals that cut through the noise, drawing attention to important events and guiding the response to maintain control and safety.
Effective alarm management is crucial for maintaining operational integrity and ensuring the safety of personnel and equipment.

## Slide 6: Types of alarms & configuration
Process Alarms: These monitor the parameters of a specific process. For example, in a water treatment plant, a low-pressure alarm may indicate a water supply issue.
Equipment Alarms: These focus on the condition of equipment. A valve position discrepancy alarm may indicate a mechanical problem.
Safety Alarms: Designed to protect human safety. In a nuclear power plant, radiation alarms are vital for the safety of workers.
Alarm Setpoints: Setpoints for alarms are configured based on the desired operating conditions. For instance, a temperature alarm might be set to trigger at 100°C.
Hysteresis: To avoid frequent alarms, hysteresis can be used. If a temperature alarm is set at 100°C with a hysteresis of 5°C, it will reset only when the temperature drops below 95°C.
Delay: Delays can be added to prevent alarms from triggering for short-lived disturbances. For example, a brief pressure spike may not warrant an alarm.
Notes: Concepts needs to be known by anyone creating an alarm

## Slide 7: Alarm selection
Lack of clear definitions from system owners
Some alarms aren’t known in the design phase. It needs to be defined after using the system and knowing the reactions and limits
Unique state machines with diverse requirements, necessitating tailored alarm configurations. (to avoid false alarm and ensure detecting anomalies)
Time-intensive configuration in the Operator Interface (OPI) for multiple state machines.
Challenges
Notes: Some systems have too little to no alarm and some systems have too many
The complexity of state machines emphasizes the need for adaptive, user-friendly configuration interfaces in the OPI.

## Slide 8: Alarm selection
Good practice
Clear communication channels between system owners, integrators and operators are essential for defining alarm criteria.
Contextual Alarm Selection
Need for adaptive, user-friendly configuration interfaces in the OPI
Notes: Collaboration with system owners is critical for obtaining precise requirements, ensuring a well-defined foundation for alarm configuration
Streamlining the configuration process in the OPI is an integral part of our responsibilities to enhance overall system efficiency.
Flow in a water cooling system isn’t relevant when in Maintenance but is critical during running. Also the delay between the Startup or Running states must be different to take into account a ramping up of the flow.

## Slide 9: Operator/end user perspective
Challenges
Determining the essential alarms for a given process
Alarm descriptions and need for annunciation
Action upon alarm activation
Balancing safety and operational flexibility with alarms and interlocks
Notes: - Operator/end user point of view : What should be there ? What description is the best ? Should there be an annunciation ?
- Balance safety/freedom of movement with alarms and interlocks
- Alarm / interlock role needs clarification over the whole facility
- Force mode to avoid being annoyed by interlocks
Consequence, the person in charge doesn’t know what’s happening and how to react

## Slide 10: Operator/end user perspective
Good practice
Bring operator and maintenance teams in the design phase.
Operators should actively participate in defining alarm descriptions, ensuring a user-centric approach
Add tooltip/details and instructions on how to react when the alarm appear
Alarms description should at least also contain the device name and its location
Notes: Thoughtful alarm descriptions and annunciations enhance operator understanding and response time
Striking a balance between safety measures and operational freedom is crucial for maintaining efficiency
Good practice, what to do when the alarm arrives
It is possible to write different action over one alarm - Targets different group of person reading the alarm
Add a « Force » operation mode to devices to overwrite interlocks for system availability

## Slide 11: Alarm flooding
Challenges
Simultaneous triggering of numerous alarms is a potential issue
Leads to information overload and hinder the identification of critical alarms amidst the noise
Crucial alerts being lost in the flood of information
Interconnection between systems may create a domino effect, amplifying the impact of a single triggering event
Network stability
Notes: Alarm fatigue is sensory overload when clinicians are exposed to an excessive number of alarms, which can result in desensitization to alarms and missed alarms.
Consequence : alarm fatigue, lack of protection and responsivness

## Slide 12: Alarm flooding
Good practice
Add delays and hysteresis
Prioritization strategies (e.g., giving precedence to critical infrastructure alarms over process alarms)
Implementation of smart filtering mechanisms, categorization, shelving
Addressing interconnection challenges to prevent cascading effects
Grouping high priority alarms
Notes: Alarm Prioritization: Alarms should be prioritized based on their criticality and logic. Critical alarms, like those related to safety, should take precedence over non-critical ones.
Alarm Categorization: Alarms can be categorized as process-related, equipment-related, or safety-related.
Alarm Shelving: Operators should be able to temporarily suppress less critical alarms during certain conditions. For example, in a manufacturing facility, certain alarms can be shelved during equipment maintenance.
Smart filtering can involve machine learning algorithms to adaptively prioritize alarms based on historical data and criticality.

## Slide 13: Alarm handling best practices
Training and awareness: Regular training ensures that users understand the alarms and know how to respond.
Alarm flood control: Implement strategies to prevent alarm floods during process upsets.
Alarm rationalization: Periodically review alarms to ensure they are necessary and not redundant.

## Slide 14: End.
Thank you for your attention.